## MAL
CHECK LIST
132 KV Line Protection
Name of the Substation |  | 220/132/33KV Kalyaneswari S/S
Date
Line No. |  |  | MAL+IMPEX
MB Isolator Close Request |  |  |  |  | MB Isolator Open Request
Functions |  | Status |  |  | Functions | Status
A | CB Open Status | 1 |  | A | CB Open Status | 1
B | MB Close Request | 1 |  | B | MB Open Request | 1
Final Output = A.B |  | TRUE |  | Final Output = A.B |  | TRUE
Checking Remarks |  |  |  | Checking Remarks
Line Isolator Close Request |  |  |  |  | Line Isolator Open Request
Functions |  | Status |  | Functions |  | Status
A | CB Open Status | 1 |  | A | CB Open Status | 1
B | Earth Switch Open | 1 |  | B | Earth Switch Open | 1
C | Line Iso Close Request | 1 |  | C | Line Iso Open Request | 1
Final Output = (A.B).C |  | TRUE |  | Final Output = (A.B).C |  | TRUE
Checking Remarks |  | OK |  | Checking Remarks |  | OK
CB CLOSE ORDER |  |  |  | TB ISOLATOR CLOSE ORDER
Functions |  | Status |  | Functions |  | Status
A | Bus Bar Protection Relay Operated | 0 |  | A | Bus-Couple Main Bus Isolator Close | 1
B | Protection of Gr. A Trip Relay Operated | 0 |  | B | Bus-Coupler CB Open | 0 |  |  | AND(F24,F25,F26,F27,F28)
C | Protection of Gr. A Trip Relay Operated | 0 |  | C | Bus-Couple Transfer Bus Isolator Close | 1
D | A/R Lockout Relay Operated | 0 |  | D | Bay Line Earth Switch Open | 1 |  |  | AND((OR((AND(F24,F25,F26,F27,F28)),(AND(F29,F30,F31)))),F32)
E | D/L Charging Mode | 1 |  | E | All Bay TB Isolator Open | 1 |  |  | AND(F29,F30,F31)
F | Dead Line | 0 |  | F | Bus-Coupler CB Open | 1
G | Live Line Charging Mode | 0 |  | G | All Bay TB Isolator Open | 1
H | Check Syncho. | 1 |  | H | Bay Line Earth Switch Open | 1
I | CB close Request | 1 |  | I | TB Isolator Close Request | 1
J | CB Open Position | 1
Final Output = (A+B+C+D)' . [{(E.F)+(G.H)}.I] . J |  | FALSE |  | Final Output = [(A.B.C.D.E)+(F.G.H)].I |  | TRUE
Checking Remarks |  | ok |  | Checking Remarks
TB ISOLATOR OPEN ORDER |  |  |  | Earth Switch Interlock Permissive
Functions |  | Status |  | Functions |  | Status
A | Bus-Couple Main Bus Isolator Close | 0 |  | A | CB Open | 1
B | Bus-Coupler CB Open | 0 |  | B | Line Under Voltage | 1
C | Bus-Couple Transfer Bus Isolator Close | 0 |  | Final Output = A.B |  | TRUE
D | Bay Line Earth Switch Open | 1 |  | Checking Remarks |  | OK
E | All Bay TB Isolator Open | 0
F | Bus-Coupler CB Open | 1
G | All Bay TB Isolator Open | 1
H | Bay Line Earth Switch Open | 1
I | TB Isolator Open Request | 1
Final Output = [(A.B.C.D.E)+(F.G.H)].I |  | TRUE
Checking Remarks
NIT Selection Switch
Functions |  | Status
|  | Position of the Latch | Bay in NI Position | Bay in Transfer Position | Bay in IT Position | Bay in Normal Position | Bay in Inter Position
Final Output Equation
A | Line Isolator Closed | 1 | TRUE | FALSE | TRUE | FALSE | TRUE | A' | FALSE
A' | Line Isolator Open | 0 | [5 empty] | B' | FALSE
C | Bay Normal | 1 | [5 empty] | E (A' . B) | FALSE | 0
B | Line TB Closed | 1 | [5 empty] | F (A . B') | FALSE | 0
B' | Line TB Open | 0
D | Bay Transfer | 1
Checking Remarks |  | OK

## 18
CHECK LIST
132 KV Line Protection
Name of the Substation |  | 220/132/33KV Kalyaneswari S/S
Date
Line No. |  |  | 18
MB Isolator Close Request |  |  |  |  | MB Isolator Open Request
Functions |  | Status |  |  | Functions | Status
A | CB Open Status | 1 |  | A | CB Open Status | 1
B | MB Close Request | 1 |  | B | MB Open Request | 1
Final Output = A.B |  | TRUE |  | Final Output = A.B |  | TRUE
Checking Remarks |  | OK |  | Checking Remarks |  | OK
Line Isolator Close Request |  |  |  |  | Line Isolator Open Request
Functions |  | Status |  | Functions |  | Status
A | CB Open Status | 1 |  | A | CB Open Status | 1
B | Earth Switch Open | 1 |  | B | Earth Switch Open | 1
C | Line Iso Close Request | 1 |  | C | Line Iso Open Request | 1
Final Output = (A.B).C |  | TRUE |  | Final Output = (A.B).C |  | TRUE
Checking Remarks |  | OK |  | Checking Remarks |  | OK
CB CLOSE ORDER |  |  |  | TB ISOLATOR CLOSE ORDER
Functions |  | Status |  | Functions |  | Status
A | Bus Bar Protection Relay Operated | 0 |  | A | Bus-Couple Main Bus Isolator Close | 1
B | Protection of Gr. A Trip Relay Operated | 0 |  | B | Bus-Coupler CB Open | 0 |  |  | AND(F24,F25,F26,F27,F28)
C | Protection of Gr. A Trip Relay Operated | 0 |  | C | Bus-Couple Transfer Bus Isolator Close | 1
D | A/R Lockout Relay Operated | 0 |  | D | Bay Line Earth Switch Open | 1 |  |  | AND((OR((AND(F24,F25,F26,F27,F28)),(AND(F29,F30,F31)))),F32)
E | D/L Charging Mode | 1 |  | E | All Bay TB Isolator Open | 1 |  |  | AND(F29,F30,F31)
F | Dead Line | 1 |  | F | Bus-Coupler CB Open | 1
G | Live Line Charging Mode | 0 |  | G | All Bay TB Isolator Open | 1
H | Check Syncho. | 1 |  | H | Bay Line Earth Switch Open | 1
I | CB close Request | 1 |  | I | TB Isolator Close Request | 1
J | CB Open Position | 1
Final Output = (A+B+C+D)' . [{(E.F)+(G.H)}.I] . J |  | TRUE |  | Final Output = [(A.B.C.D.E)+(F.G.H)].I |  | TRUE
Checking Remarks |  | OK |  | Checking Remarks
TB ISOLATOR OPEN ORDER |  |  |  | Earth Switch Interlock Permissive
Functions |  | Status |  | Functions |  | Status
A | Bus-Couple Main Bus Isolator Close | 0 |  | A | CB Open | 1
B | Bus-Coupler CB Open | 0 |  | B | Line Under Voltage | 1
C | Bus-Couple Transfer Bus Isolator Close | 0 |  | Final Output = A.B |  | TRUE
D | Bay Line Earth Switch Open | 1 |  | Checking Remarks |  | OK
E | All Bay TB Isolator Open | 0
F | Bus-Coupler CB Open | 1
G | All Bay TB Isolator Open | 1
H | Bay Line Earth Switch Open | 1
I | TB Isolator Open Request | 1
Final Output = [(A.B.C.D.E)+(F.G.H)].I |  | TRUE
Checking Remarks
NIT Selection Switch
Functions |  | Status
|  | Position of the Latch | Bay in NI Position | Bay in Transfer Position | Bay in IT Position | Bay in Normal Position | Bay in Inter Position
Final Output Equation
A | Line Isolator Closed | 1 | TRUE | FALSE | TRUE | FALSE | TRUE | A' | FALSE
A' | Line Isolator Open | 0 | [5 empty] | B' | FALSE
C | Bay Normal | 1 | [5 empty] | E (A' . B) | FALSE | 0
B | Line TB Closed | 1 | [5 empty] | F (A . B') | FALSE | 0
B' | Line TB Open | 0
D | Bay Transfer | 1
Checking Remarks |  | OK

## 19
CHECK LIST
132 KV Line Protection
Name of the Substation |  | 220/132/33KV Kalyaneswari S/S
Date
Line No. |  |  | 19
MB Isolator Close Request |  |  |  |  | MB Isolator Open Request
Functions |  | Status |  |  | Functions | Status
A | CB Open Status | 1 |  | A | CB Open Status | 1
B | MB Close Request | 1 |  | B | MB Open Request | 1
Final Output = A.B |  | TRUE |  | Final Output = A.B |  | TRUE
Checking Remarks |  | OK |  | Checking Remarks |  | OK
Line Isolator Close Request |  |  |  |  | Line Isolator Open Request
Functions |  | Status |  | Functions |  | Status
A | CB Open Status | 1 |  | A | CB Open Status | 1
B | Earth Switch Open | 1 |  | B | Earth Switch Open | 1
C | Line Iso Close Request | 1 |  | C | Line Iso Open Request | 1
Final Output = (A.B).C |  | TRUE |  | Final Output = (A.B).C |  | TRUE
Checking Remarks |  | OK |  | Checking Remarks |  | OK
CB CLOSE ORDER |  |  |  | TB ISOLATOR CLOSE ORDER
Functions |  | Status |  | Functions |  | Status
A | Bus Bar Protection Relay Operated | 0 |  | A | Bus-Couple Main Bus Isolator Close | 0
B | Protection of Gr. A Trip Relay Operated | 0 |  | B | Bus-Coupler CB Open | 1 |  |  | AND(F24,F25,F26,F27,F28)
C | Protection of Gr. A Trip Relay Operated | 0 |  | C | Bus-Couple Transfer Bus Isolator Close | 1
D | A/R Lockout Relay Operated | 0 |  | D | Bay Line Earth Switch Open | 1 |  |  | AND((OR((AND(F24,F25,F26,F27,F28)),(AND(F29,F30,F31)))),F32)
E | D/L Charging Mode | 1 |  | E | All Bay TB Isolator Open | 1 |  |  | AND(F29,F30,F31)
F | Dead Line | 1 |  | F | Bus-Coupler CB Open | 1
G | Live Line Charging Mode | 1 |  | G | All Bay TB Isolator Open | 1
H | Check Syncho. | 1 |  | H | Bay Line Earth Switch Open | 1
I | CB close Request | 1 |  | I | TB Isolator Close Request | 1
J | CB Open Position | 1
Final Output = (A+B+C+D)' . [{(E.F)+(G.H)}.I] . J |  | TRUE |  | Final Output = [(A.B.C.D.E)+(F.G.H)].I |  | TRUE
Checking Remarks |  | OK |  | Checking Remarks
TB ISOLATOR OPEN ORDER |  |  |  | Earth Switch Interlock Permissive
Functions |  | Status |  | Functions |  | Status
A | Bus-Couple Main Bus Isolator Close | 0 |  | A | CB Open | 1
B | Bus-Coupler CB Open | 0 |  | B | Line Under Voltage | 1
C | Bus-Couple Transfer Bus Isolator Close | 0 |  | Final Output = A.B |  | TRUE
D | Bay Line Earth Switch Open | 1 |  | Checking Remarks |  | OK
E | All Bay TB Isolator Open | 0
F | Bus-Coupler CB Open | 1
G | All Bay TB Isolator Open | 1
H | Bay Line Earth Switch Open | 1
I | TB Isolator Open Request | 1
Final Output = [(A.B.C.D.E)+(F.G.H)].I |  | TRUE
Checking Remarks
NIT Selection Switch
Functions |  | Status
|  | Position of the Latch | Bay in NI Position | Bay in Transfer Position | Bay in IT Position | Bay in Normal Position | Bay in Inter Position
Final Output Equation
A | Line Isolator Closed | 1 | TRUE | FALSE | TRUE | FALSE | TRUE | A' | FALSE
A' | Line Isolator Open | 0 | [5 empty] | B' | FALSE
C | Bay Normal | 1 | [5 empty] | E (A' . B) | FALSE | 0
B | Line TB Closed | 1 | [5 empty] | F (A . B') | FALSE | 0
B' | Line TB Open | 0
D | Bay Transfer | 1
Checking Remarks |  |  | ok | OK | ok | OK | OK

## Line Differential
CHECK LIST
132 KV Line Differential Protection
Name of the Substation
Date
Line No.
MB Isolator Close Request |  |  |  |  | MB Isolator Open Request
Functions |  | Status |  |  | Functions | Status
A | CB Open Status | 1 |  | A | CB Open Status | 1
B | MB Close Request | 1 |  | B | MB Open Request | 1
Final Output = A.B |  | TRUE |  | Final Output = A.B |  | TRUE
Checking Remarks |  |  |  | Checking Remarks
Line Isolator Close Request |  |  |  |  | Line Isolator Open Request
Functions |  | Status |  | Functions |  | Status
A | CB Open Status | 1 |  | A | CB Open Status | 1
B | Earth Switch Open | 1 |  | B | Earth Switch Open | 1
C | Line Iso Close Request | 1 |  | C | Line Iso Open Request | 1
Final Output = (A.B).C |  | TRUE |  | Final Output = (A.B).C |  | TRUE
Checking Remarks |  |  |  | Checking Remarks
CB CLOSE ORDER |  |  |  | TB ISOLATOR CLOSE ORDER
Functions |  | Status |  | Functions |  | Status
A | Bus Bar Protection Relay Operated | 0 |  | A | Bus-Couple Main Bus Isolator Close | 1
B | Protection of Gr. A Trip Relay Operated | 0 |  | B | Bus-Coupler CB Open | 1 |  |  | AND(F24,F25,F26,F27,F28)
C | Protection of Gr. A Trip Relay Operated | 0 |  | C | Bus-Couple Transfer Bus Isolator Close | 1
D | A/R Lockout Relay Operated | 0 |  | D | Bay Line Earth Switch Open | 1 |  |  | AND((OR((AND(F24,F25,F26,F27,F28)),(AND(F29,F30,F31)))),F32)
E | D/L Charging Mode | 1 |  | E | All Bay TB Isolator Open | 1 |  |  | AND(F29,F30,F31)
F | Dead Line | 0 |  | F | Bus-Coupler CB Open | 1
G | Live Line Charging Mode | 0 |  | G | All Bay TB Isolator Open | 1
H | Check Syncho. | 1 |  | H | Bay Line Earth Switch Open | 1
I | CB close Request | 1 |  | I | TB Isolator Close Request | 0
J | CB Open Position | 0
Final Output = (A+B+C+D)' . [{(E.F)+(G.H)}.I] . J |  | FALSE |  | Final Output = [(A.B.C.D)+(F.G.H)].I |  | FALSE
Checking Remarks |  |  |  | Checking Remarks
TB ISOLATOR OPEN ORDER |  |  |  | Earth Switch Interlock Permissive
Functions |  | Status |  | Functions |  | Status
A | Bus-Couple Main Bus Isolator Close | 0 |  | A | CB Open | 1
B | Bus-Coupler CB Open | 0 |  | B | Line Under Voltage | 1
C | Bus-Couple Transfer Bus Isolator Close | 0 |  | Final Output = A.B |  | TRUE
D | Bay Line Earth Switch Open | 1
E | All Bay TB Isolator Open | 0
F | Bus-Coupler CB Open | 1
G | All Bay TB Isolator Open | 1
H | Bay Line Earth Switch Open | 1
I | TB Isolator Open Request | 1
Final Output = [(A.B.C.D)+(F.G.H)].I |  | TRUE
Checking Remarks
NIT Selection Switch
Functions |  | Status
|  | Position of the Latch | Bay in NI Position | Bay in Transfer Position | Bay in IT Position | Bay in Normal Position | Bay in Inter Position
Final Output Equation
A | Line Isolator Closed | 1 | TRUE | FALSE | TRUE | FALSE | TRUE | A' | FALSE
A' | Line Isolator Open | 0 | [5 empty] | B' | FALSE
C | Bay Normal | 1 | [5 empty] | E (A' . B) | FALSE | 0
B | Line TB Closed | 1 | [5 empty] | F (A . B') | FALSE | 0
B' | Line TB Open | 0
D | Bay Transfer | 1
Checking Remarks

## Transformer Prot
CHECK LIST
132 KV Transformer Protection
Name of the Substation
Date
Line No.
MB Isolator Close Request |  |  |  | MB Isolator Open Request
Functions |  | Status |  |  | Functions | Status
A | CB Open Position | 1 |  | A | CB Open Position | 1
B | MB Close Request | 1 |  | B | MB Open Request | 1
Final Output = A.B |  | TRUE |  | Final Output = A.B |  | TRUE
Checking Remarks |  |  |  | Checking Remarks
Transformer Isolator Close Request |  |  |  | Transformer Isolator Open Request
Functions |  | Status |  | Functions |  | Status
A | CB Open Position | 1 |  | A | CB Open Position | 1
B | T Close Request | 1 |  | B | T Close Request | 1
Final Output = A.B |  | TRUE |  | Final Output = A.B |  | TRUE
Checking Remarks |  |  |  | Checking Remarks
CB CLOSE ORDER |  |  |  | TB ISOLATOR CLOSE ORDER
Functions |  | Status |  | Functions |  | Status
A | Bus Bar Protection Relay Operated | 0 |  | A | Bus-Couple Main Bus Isolator Close | 1
B | Protection of Gr. A Trip Relay Operated | 0 |  | B | Bus-Coupler CB Open | 1 |  |  | AND(F24,F25,F26,F27,F28)
C | Protection of Gr. B Trip Relay Operated | 0 |  | C | Bus-Coupler Transfer Bus Isolator Close | 1
D | D/L Charging Mode | 1 |  | D | Bay CB Close Position | 0 |  |  | AND(F29,F30,F31)
E | Dead Line | 1 |  | E | All Bay TB Open | 1
F | Live Line Charging Mode | 1 |  | F | Bus Coupler CB Open | 0
G | Check Syncho. | 1 |  | G | All Bay TB Open | 1
H | CB close Request | 1 |  | H | TB Isolator Close Request | 1
I | CB Open Position | 1
Final Output = (A+B+C)' . [{(D.E)+(F.G)}.H] . I |  | TRUE |  | Final Output = [(A.B.C.D.E)+(F.G)].H |  | FALSE
Checking Remarks |  |  |  | Checking Remarks
TB ISOLATOR OPEN ORDER
Functions |  | Status
A | Bus-Couple Main Bus Isolator Close | 1
B | Bus-Coupler CB Open | 1
C | Bus-Coupler Transfer Bus Isolator Close | 1
D | Bay CB Close Position | 1
E | All Bay TB Open | 1
F | Bus Coupler CB Open | 0
G | All Bay TB Open | 0
I | TB Isolator Open Request | 1
Final Output = [(A.B.C.D.E)+(F.G)].I |  | TRUE
Checking Remarks
NIT Selection Switch
Functions |  | Status
|  | Position of the Latch | Bay in NI Position | Bay in Transfer Position | Bay in IT Position | Bay in Normal Position | Bay in Inter Position
Final Output Equation
A | Transformer Isolator Closed | 0 | FALSE | TRUE | TRUE | FALSE | FALSE | A' | TRUE
A' | Transformer Isolator Open | 1 | [5 empty] | B' | FALSE
C | Bay Normal | 0 | [5 empty] | E (A' . B) | TRUE | 1
B | Line TB Closed | 1 | [5 empty] | F (A . B') | FALSE | 0
B' | Line TB Open | 0
D | Bay Transfer | 1
Checking Remarks

## Bus Coupler
CHECK LIST
132 KV Transformer Protection
Name of the Substation
Date
Line No.
MB Isolator Close Request |  |  |  | MB Isolator Open Request
Functions |  | Status |  |  | Functions | Status
A | CB Open Position | 1 |  | A | CB Open Position | 1
B | MB Close Request | 1 |  | B | MB Open Request | 1
Final Output = A.B |  | TRUE |  | Final Output = A.B |  | TRUE
Checking Remarks |  |  |  | Checking Remarks
TB Isolator Close Request |  |  |  | TB Isolator Open Request
Functions |  | Status |  | Functions |  | Status
A | CB Open Position | 1 |  | A | CB Open Position | 1
B | TB Close Request | 1 |  | B | TB Close Request | 1
Final Output = A.B |  | TRUE |  | Final Output = A.B |  | TRUE
Checking Remarks |  |  |  | Checking Remarks
Bus-Section B Isolator Close |  |  |  | Bus-Section B Isolator Open
Functions |  | Status |  | Functions |  | Status
A | Bus-Section A Isolator Open | 1 |  | A | Bus-Section A Isolator Open | 1
B | MB 1 Isolator Open | 1 |  | B | MB 1 Isolator Open | 0 |  |  | AND(F24,F25,F26,F27,F28)
C | MB 2 Isolator Open | 1 |  | C | MB 2 Isolator Open | 1
D | MB 3 Isolator Open | 0 |  | D | MB 3 Isolator Open | 1 |  |  | AND(F29,F30,F31)
E | MB 4 Isolator Open | 1 |  | E | MB 4 Isolator Open | 1
F | MB 5 Isolator Open | 1 |  | F | MB 5 Isolator Open | 1
G | MB 6 Isolator Open | 1 |  | G | MB 6 Isolator Open | 1
H | Bus-Section B Isolator Close request | 1 |  | H | Bus-Section B Isolator Open request | 0
Final Output = (A+(B.C.D.E.F.G)).H |  | TRUE |  | Final Output = (A+(B.C.D.E.F.G)).H |  | FALSE
Checking Status |  |  |  | Checking Status
Bus-Section A Isolator Close |  |  |  | Bus-Section A Isolator Open
Functions |  | Status |  | Functions |  | Status
A | Bus-Section B Isolator Open | 1 |  | A | Bus-Section B Isolator Open | 1
B | MB 8 Isolator Open | 1 |  | B | MB 8 Isolator Open | 1
C | MB 9 Isolator Open | 1 |  | C | MB 9 Isolator Open | 1
D | MB 10 Isolator Open | 0 |  | D | MB 10 Isolator Open | 0
E | MB 11 Isolator Open | 1 |  | E | MB 11 Isolator Open | 1
H | Bus-Section A Isolator Close Request | 1 |  | H | Bus-Section A Isolator Close Request | 1
Final Output = (A+(B.C.D.E.)).F |  | TRUE |  | Final Output = (A+(B.C.D.E.)).F |  | TRUE
Checking Status |  |  |  | Checking Status
Bus- Coupler Breaker Close Order
Functions |  | Status | [6 empty] | 0
A | A/R Lockout Operated | 0 | [6 empty] | 1
B | LBB Protection Operated | 0 | [6 empty] | 1
C | Trip Circuit -1 Faulty | 0 | [6 empty] | 1
D | Trip Circuit -2 Faulty | 0 | [6 empty] | 1
E | B/C CB Close Request | 1 | [6 empty] | 1
F | D/L Charging Mode | 1 | [6 empty] | 1
G | Dead Line | 1 | [6 empty] | 1
H | Live Line Charging Mode | 0 | [6 empty] | 0
I | Check Syncho | 1 | [6 empty] | 1
J | B/C CB Open Position | 1 | [6 empty] | 1
Final Formula = A'.B'.C'.D'.((F.G+H.I).E).J |  | TRUE
Checking Remarks
NIT Selection Switch
Functions |  | Status
|  | Position of the Latch | Bay in NI Position | Bay in Transfer Position | Bay in IT Position | Bay in Normal Position | Bay in Inter Position
Final Output Equation
A | Transformer Isolator Closed | 0 | FALSE | TRUE | TRUE | FALSE | FALSE | A' | TRUE
A' | Transformer Isolator Open | 1 | [5 empty] | B' | FALSE
C | Bay Normal | 0 | [5 empty] | E (A' . B) | TRUE | 1
B | Line TB Closed | 1 | [5 empty] | F (A . B') | FALSE | 0
B' | Line TB Open | 0
D | Bay Transfer | 1
Checking Remarks